[image: image1.wmf]â










REVISED:     3/07









SUPERSEDES:   9/06
“G” SERIES XE "Cover Sheet" 

INSTALLATION & SERVICE INSTRUCTIONS

AIR CONDITIONING/HEAT PUMP

COMPRESSORS
BRISTOL 
[image: image11.wmf] 

Family

 

Reciprocating 

Compressors 

Serial Number 

System

 

Scroll Compressors 

Serial Number 

System

 

Example:

 

S3702K00001

 

 

S

 

= Scroll Technologies

 

 

37

 

=  Production Week

 

 

02

 

= Year

 

 

K

 

= State (Arkansas)

 

 

0001

 

= Sequence No. 

of

 

 

 

 

Units Built During Week

 

Julian Date of 

Manufacture:

 

Year Manufactured

 

Manufacturing

 

Location

 

Daily Unit Manufactured

 

00235

 

00235 = 235th Unit of the Day

 

108

 

02

 

2

 

02 = 2002

 

108 = April 18th

 

0 or 2 = Bristol

 

1 or 3 = Sparta

 


COMPRESSORS, INC.


BRISTOL COMPRESSORS, INC.

BRISTOL, VIRGINIA  24202

(276) 466-4121

FAX (276) 645-2423

www.bristolcompressors.com

Index


Page XE "Index" 
Cover Sheet
1

Index
2

Compressor Model Number System
3

Before Condemning a Compressor that Fails to Start
4

Installation Procedures After compressor has Been Verified as Faulty
4 - 9

Worst Case Condition Checks
8

How to Check Superheat
8

Check Filter Driers for Contamination
9

Module Electrical Schematics and Other Information


Summary of Electronic Modules
10


AE, 31AA, 41AA or INT 369R Protection Modules (Parallel Sensors)


Dual Power Terminal, Full and Part Winding Start Models
11


AE, 31AA, 41AA or INT 369R Protection Modules (Parallel Sensors)


Dual Power Terminal (WYE-Delta) Models
12


AE, 31AA, 41AA or INT 369R Protection Modules (Parallel Sensors)


Single Power Terminal Models
13


AE, 30AA, 40AA or INT 369R Protection Modules (Series Sensors)


Single Power Terminal Models
14


AE, 31AA, 41AA or INT 369R Modules (Parallel Sensors)


Two-Speed Models
15


AE, 30AA, 40AA or INT 369R Modules (Series Sensors)


Two-Speed Models
16


“G” Series Internal Line Break Models
17


H*NG, H*BG and H*5G Housing Configuration
17


Replacing Module Protected Compressor with Line Break Compressor
17-18


Wiring a Two-Speed “G” for Single-Speed Operation
19

Parts and Accessories for “G” Series Compressors
20

Rotalock Adapters and Valve Part Numbers and Drawings
21

Compressor Mounting Information
22

Explanation of the European Pressure Equipment Directive (PED)
22

Pressure-Temperature Relation Chart
23


WARNING:  Cannot use ICM parallel motor protection modules, part numbers 241730 or 241731, with Kriwan sensors (cold resistance of 30-100 ohms for parallel sensors) because the modules have “shorted sensor protection” that does not allow operation below 500 ohms.

COMPRESSOR MODEL NUMBER SYSTEM XE "Compressor Model Number System" 
H 2 9 B 18U A B C A


Mounting Feet Dim
A = 7.5 x 7.5
B = 4.8 x 8.0
C = 8.4 x 9.8
E = 9.5 x 9.5



F = 10.5 x 10.5
H = 7.5 x 21.5
J = 7.5 x 22.5
X = 8.8 x 6.1


Electrical Characteristics
A = 115-1-60

M = 220/200-3-50



B = 230-1-60

N = 380/415-3-50



C = 230/208-1-60

P = 240/200-1-50



D = 230/208-3-60 (220/200-3-50)
T = 208-1-60



E = 460-3-60 (380/415-3-50)
U = 220/380-3-60



F = 575-3-60 (500-3-50)
V = 460/380-3-60 (380/415-3-50)



G = 200-1-60

W = 380/460-3-60



H = 265-1-60 (220/240-1-50)
X = 380-3-60



J = 230/208-1-50

Y = 230/208-3-60 (No 50 Hz)



K = 220/240-1-50



L = 230/200-3-60 (220/200-3-50)


Motor Protector
B = Internal Line Break



P = Pilot Duty – Solid State



R = Pilot Duty – Solid State (2nd Generation)



T = Pilot Duty – Internal Thermostat and External Sensing Elements


Motor Type
A = PSC Permanent Split Capacitor
F = PWS 3 Phase – Part Winding Start



B = CSR Capacitor Start/Cap. Run
G = 3 Phase 2/4 Pole (2 Speed)



C = RSCR Resistance Start/Cap. Run
J = 1 Phase 2/4 Pole (2 Speed)



D = AL 3 Phase-Across the Line
K = 3 Phase – Dual Voltage



E = CSIR Cap. Start/Induction Run
L = 3 Phase – WYE DELTA


Capacity
193 = 19,000 BTU/Hr., 244 = 240,000 BTU/Hr. When 5-7 digits are numerical/



19Q = 19+3-0’s in “Quiet Version” – 19,000 BTU/Hr. “Quiet”


Family
A = Model A Reciprocating
J = Benchmark Reciprocating (<44K)



B = Model B Reciprocating
K = Benchmark Reciprocating (>44K)



C = Scroll (<42K)

R = Scroll (>42K)



D = Dual Compressor Application
S = Single Cylinder Series



G = Model G Reciprocating
T = Two Cylinder Series


Generation
B = Second Generation – No PRV (Except G Series)
2 = Third Generation – Basic Standard Model



D = Dual Compressor Application (Single & Interconnected)
3 = Fourth Generation – Basic Standard Model



E = High Efficiency


4 = Basic Standard Model – Improved Sound



M = Alternate Pressure Relief Valve

5 = Inertia Series – Standard Model



N = No Pressure Relief Valve (Except G Series)
6 = Inertia Series – High Efficiency Model



O = Basic Standard Model

7 = Inertia Series – Second Generation High Efficiency Model



P = Basic Standard Model – Upgrade Plus
8 = Fifth Generation – Basic Standard Model Upgrade



1 = Second Generation – Basic Standard Upgrade
9 = Sixth Generation – Basic Standard Model Upgrade


Type of Refrigerant
1 = R12

5 = R502 or Alternate Replacement Refrigerant R402B



2 = R22

6 = R404A or Alternate Replacement Refrigerant R507



4 = R134a

7 = R507C
8 = R410A


Refrigeration Application
H = High Temperature
S = High Temperature (One Capacity / 1, 2, 3 or 4 cylinder) Half/Single



M = Medium Temperature
T = High Temperature (Two Capacities / 2 or 4 cylinder) Twin/Single



L = Low Temperature



BEFORE CONDEMNING A COMPRESSOR THAT FAILS TO START XE "Before Condeming a Compressor That Fails to Start" :

1.
Verify all the following components are OK:

A.
Contactor


B.
Winding resistance within manufacturer’s specification (assure compressor is cool to the touch)


C.
Compressor not grounded via ohmmeter/Megger, etc.


D.
Compressor power terminals are tight and secure


E.
Check for hot spots in system wiring (wire insulation melted, connectors/insulators melted, etc.)

2.
Verify lock rotor pull-down voltage (LRPDV)


Always check LRPDV before removing the old or new replacement compressor.  If the LRPDV reduces the supply voltage to the compressor below the “guaranteed to start” voltage of the compressor (three-phase 230/208 LRPDV is 187V), the power supply must be corrected before removing the compressor.  Always check all three legs, T1 to T2, T1 to T3, and T2 to T3.  To perform this test on two-speed compressors, you should wire for single-speed operation as illustrated on page 19.


Procedure to check for LRPDV:  (Warning:  Make sure unit is properly grounded before proceeding!)

A.
Connect a voltmeter to the T1 terminal and T2 terminal of the compressor.


B.
Make sure the terminal cover and retainer is in place (see warning page 7) then apply power to the compressor.  If motor protector trips, allow time for reset before continuing.


C.
If the voltage at the compressor terminals does not pull down below the LRPDV and the compressor still does not start, it is electrically or mechanically faulty.


D.
Repeat A through C for voltage at T1-T3 and T2-T3.

INSTALLATION PROCEDURES AFTER COMPRESSOR HAS BEEN VERIFIED AS FAULTY: XE "Installation Procedures After Compressor has Been Verified as Faulty" \r "Installation_Procedures_Faulty" 

The following instructions are general but include major points of consideration that will ensure proper installation and protect you from possible personal injury.  Please use this as a checklist, taking each item in its order before proceeding to the next.  If more information is required, please call Bristol Compressors Service Department.



1.
VERIFY PROPER APPLICATION.  Verify that the compressor being replaced and the Bristol compressor have a like capacity for the refrigerant being used and that the voltage and frequency characteristics are the same.  Consult your wholesaler if you have any questions about proper compressor application.




2.  
DETERMINE CAUSE OF INITIAL FAILURE.  In order to prevent a second failure, the cause of the original failure must be determined.  Identify the cause and make the necessary repairs.


A.
BEFORE REMOVING THE FAULTY COMPRESSOR:  Remove refrigerant charge using proper recovery procedures.  Call 1-800-441-9450 for the name of the nearest Dupont authorized distributor, or 1-800-631-8138 for Genetron Representative or 1-800-ASK-KLEA (ICI) for information on refrigerant reclaim program.


B.
Remove the electrical leads from the compressor.  Note the terminal to which each wire is connected.


C.
During the next operation, the access ports should be open so that pressure does not build up in the system.  Use a high temperature torch to sweat the suction line and the discharge line loose from the compressor.


D.
Assure excessive oil does not remain in the system, measure oil in the failed compressor and, if oil is low, flush excess from system (or see step 15 as an alternative).  Good indicators of excess oil are:  violent vibration and/or high variable sound as the extra oil moves through the system.



CAUTION:  The compressor may contain harmful acids ( be sure to handle with extreme care using proper protection equipment.  After confirming oil charge level, return oil to the compressor and install suction and discharge rotalock caps.  Copper tube fittings should be brazed closed.  This is needed to prevent further contamination of the compressor and to prevent spillage from the compressor.


3.  
MOUNT THE NEW COMPRESSOR.  Do not remove dust cover or rubber shipping plugs until all other connections have been completed (i.e., filters installed and all tubing changes made per Steps 3, 4, 5 and 6).  Compressor should not be open to the atmosphere for more than 15 minutes.  Be sure to use the new mounting grommets that were shipped with the compressor.  If the mounting sleeves shipped with the compressor are used, the mounting bolts will bottom out when tight.  Use care not to over-compress the mounting grommets when the mounting sleeves cannot be used.


4.  
INSTALL FILTER DRIERS.  Bristol Compressors recommends the use of adequately sized liquid and suction line driers anytime a compressor is replaced.  If the new compressor is used to replace a compressor with a burned motor, the use of high acid neutralizing filter drier is recommended.  For heat pumps, a suction filter drier must be installed between the accumulator and the compressor suction inlet.  In addition, a bi-directional heat pump liquid line drier or factory recommended driers must be installed.  NOTE:  ALWAYS REMOVE OLD FILTER DRIERS.


5.  
ATTACH SUCTION AND DISCHARGE LINES (FOR UNITS WITH ROTALOCKS).  




After all housing pressure is relieved, remove the rotalock caps from the suction and discharge line fittings on the compressor.  On rotalock fittings, be sure the Teflon fiber seal located on the face of the fittings are seated properly and are not damaged.  Attach the suction and discharge line to the compressor as follows:


A.
Align the suction and discharge line with the fitting on the compressor to ensure a good seal when the lines are tightened.  In some cases, it may be necessary to modify the system tubing to ensure proper alignment.


B.
Tighten the nuts on the suction and discharge line until you detect metal-to-metal contact between the fittings.  At this point, the Teflon fiber seal has been totally compressed.  Tighten the nuts an additional 1/4 turn to ensure good contact and a proper seal.






6.  
BRAZE ON SUCTION AND DISCHARGE LINES.  Carefully remove the rubber plugs from the suction and discharge line fittings.  Flow an inert gas, such as nitrogen or CO2, through the system at approximately 2 psig to reduce the possibility of oxidation inside the tubing.  Braze on the suction and discharge lines following the recommendation listed below (if a process tube is provided, it should be brazed shut after the system has been charged):

COPPER TUBING:
If additional copper tubing is required, use only clean, dehydrated refrigeration grade tubing with sealed ends.

BRAZING ALLOYS: 
CAUTION:  Do not use 95/5, 50/50 or 40/60 soft solder for brazing.  Use Sil-Fos or Phos Copper, or similar brazing alloys with high tensile strength on copper welds only.  Weld steel to copper only with silver brazing alloys.

BRAZING PROCEDURE:
To ensure properly brazed joints, Bristol Compressors recommends that the following steps be used:


a.  
Exercise extreme care when cutting and forming tubes to keep dirt, filings, and other contaminants from entering the system.


b.   
Do not use excessive amounts of brazing alloy as some of the excess may penetrate the joint and enter the system.


c.   
If flux must be used, take necessary precautions to ensure that the flux does not enter the system.


d.   
Use damp cloths or other heat absorbent material to ensure that the factory brazed joints on the compressor do not become damaged.  If damp cloths are used, take care not to allow moisture to enter the system.


e.    Do not overheat brazed joints as excess heat will cause formation of copper oxide on the inside wall of the tubing.  Flow an inert gas through the system, as explained above.



7.  
If the Bristol compressor is being used as a replacement for a semi-hermetic using an oil pressure switch, remove the switch from the unit.  The Bristol compressor requires no such switch.


8.  
CHECK SYSTEM FOR LEAKS.  After installation is complete, pressurize the system to 75 psig using nitrogen and a few ounces of system refrigerant.  Check for leaks using a halide torch, soap bubbles or an electronic halogen leak detector.  When all connections test satisfactorily, release pressure using proper recovery procedures, then proceed to next step.



9.  
EVACUATE THE SYSTEM.  Use a vacuum pump designed for this purpose.  Vacuum must be pulled on the discharge (high side) and suction (low side) of the system.  Evacuate to 200 microns or lower.


10.  
CHARGE THE SYSTEM.  When a vacuum of at least 200 microns is reached, close gauge valve, remove vacuum pump, and break the vacuum using system refrigerant vapor.  Never dump liquid refrigerant into the compressor.  Liquid can be used to break the vacuum if it is connected to the liquid line, not the discharge line.



Charge the system according to the manufacturer's specifications.  Be sure to compensate the charge for the addition of the filter drier.  The preferred superheat should be 18-20°F (10-11°C) at the compressor on a system with a TXV, see Step 16.



WEIGHING in the system charge to the factory specification will help point out system faults that may still exist.



11. 
INSTRUCTIONS FOR CHANGING MOTOR PROTECTION MODULES IN BRISTOL “G” SERIES COMPRESSORS: (Refer to page 10 for module summary chart)



WARNING:  Assure power is turned off; sensor terminals can be hot to ground!

A.
H*NG094, H*NG104 and H*NG124 (12” diameter housing)


1.
Disconnect the two wires from the two-pin hermetic terminal in the compressor housing.


2.
Remove the module mounting screws and remove the module and connecting wires.


3.
Install the new module using the same mounting screws.  Two sensor lead wires should be attached to the designated module terminals per the appropriate wiring diagram in this booklet.  The free ends should be fitted onto the two hermetic terminals.  Either wire on either terminal is OK.


4.
Follow appropriate wiring diagram in this booklet for connections to unit power and control circuit.


B.
H*NG144 thru H*NG294 and H*5G184 thru H*5G294 (all 14” diameter housings)


1.
Before disconnecting the four sensor leads, please note the top left pin of the four-pin terminal is in the “COMMON” pin.


2.
Disconnect the four-wire block connector from the four-pin hermetic terminal in the compressor housing.


3.
Remove the module mounting screws and remove the module and connecting wires.


4.
Install the new module using the same mounting screws.  Make the sensor lead wire connections as follows, depending on the particular module being installed:  (a)  If the module includes one black wire and three orange wires, connect the black wire to the common terminal as determined in Step 1 above.  Connect the other three orange wires to the three remaining pins in any order.


5.
Follow appropriate wiring diagram in this booklet for connections to unit power and control circuit.


12.  
All electrical components should be checked.  If faulty, or signs of degradation are found, they should be replaced.  Check all connections and terminals for tightness.  Use only a new Bristol protection module when using Bristol replacement compressors.


13.  
Check pages 11 thru 16, 18 and 19 for correct wiring diagram.


WARNING:  Do not remove "C" sensor wire on AE or 31AA modules or "S1" sensor wire on AE or 30AA modules.  These terminals are internally connected to line voltage, can be "hot" to ground.






VERY IMPORTANT:  Before applying power to the compressor, be sure to perform a functional check of the motor protection system.  This can be done by wiring the provided module as shown with the appropriate schematic, leaving the power supply wires from the main contactor open ( NO POWER TO COMPRESSOR.  Then apply control circuit power.  Main contactor should pull-in (or energize), assuming all other safeties are closed.  Next, carefully remove module sensor wires from compressor (only one necessary unless block connector is used).  TAKE CARE NOT TO SHORT LEAD AGAINST HOUSING.  The main contactor should immediately open.  If this does not happen, thoroughly check control wiring unit until this functional check is positive.  Then complete the system wiring.


WARNING:  Replacement compressor failure may result if you fail to check the total electrical system against the equipment manufacturer’s service manual and the Bristol compressor wiring diagram before start-up.  Make sure the electrical characteristics of the Bristol replacement compressor are the same as the original compressor.


14.  
Bristol recommends a four-minute time delay on break in series with the contactor to prevent short cycling of the compressor from possible defective or improper operation of controls.



15.  
Confirm oil is in compressor sight glass by depressing Schrader.  After approximately two hours running time, check the sight glass to be sure there is adequate oil in the compressor.  If oil level is not visible, add Shrieve Zerol 150T oil until the level reaches the approximately mid-point of sight glass.  If oil level is above sight glass, remove oil until level is approximately mid-point of sight glass.


16.  
WORST CASE CONDITION CHECKS XE "Worst Cast Condition Checks" . 




HEAT PUMP 


STEP 1:
Operate system in the heating mode with outdoor fan disconnected.


STEP 2:
Run system until the designed winter condition in your area is reached (may need to cover coil for this test).


STEP 3:
Check suction superheat 6" from compressor inlet.


STEP 4:
Superheat should not drop below 5F° (3°K) (prefer no lower than 10F° [6°K]).


STEP 5:
Sump temperature should always be 50F°  (28°C) or higher above saturated suction temperature.

EXAMPLE:  "R-22"



38 psig =
16F° (-9°C)
= SATURATED SUCTION




+ 50F° (28°K)
= MINIMUM TEMP. DIFFERENCE

               


66F° (19°C)
= MINIMUM SUMP TEMPERATURE



COOLING MODE  (HEAT PUMP):


STEP 1:
Operate system in cooling mode with indoor fan disconnected and repeat steps 3, 4 and 5.



AIR-CONDITIONING ONLY UNITS


STEP 1:
Operate system in the cooling mode with indoor fan disconnected and repeat steps 3, 4 and 5.


[image: image2.wmf] 

TAKE SUCTION 

 

TEMPERATURE

 

6" TO 12"

 

FROM

 COMPRESSOR

 

NOTE:

 

 58°F

 

-

38°F

 

 20°F

 

FOR THE HARD TO GET

 

TO COMPRESSOR TAKE

 

TEMPERATURES AND

 

PRESSURES HERE,

 

AIR CONDITIONING

 

UNIT ONLY

 

CONVERT SUCTION

 

    PRESSURE TO

 

    TEMPERATURE

 

65 PSIG = 38°F (3°C)

 

 

 

     SUPERHEAT

 

HOW TO CHECK SUPER

HEAT

 

58°F

 

  DIGITAL

 

THERMOMETER

 

(14° C)

 

 (14°C)

 

(

-

 3°C)

 

 (11°K)

 





17.  
CHECK FILTER DRIER FOR CONTAMINATION XE "Check Filter Drier for Contamination" .



A.
Suction Line Filter:  If internal contamination is heavy, the suction line filter drier may become clogged and ineffective.  Check the pressure drop across the filter drier after approximately 8 hours running time and, if it exceeds 2 psig, replace.



B.
Liquid Line Filter:  Always replace the original equipment liquid line filter drier(s).  If the OEM liquid line drier(s) is not removed from the system, a restriction most likely will result.  Just a slight restriction in this filter will reduce the efficiency of the system.  A large restriction will cause the suction pressure and discharge pressure to be reduced.  This reduction in pressure will occur only with a properly charged system (i.e., refrigerant weighed in to the OEM specifications).  An overcharged system will increase pressures when there is a restriction in the liquid line.  The service person tends to add more charge to the system to increase the suction pressure.  Normally any charge added above the OEM specifications will increase the suction pressure due to the discharge pressure increasing, but in the case of a restriction, charge can be added to a point the system shuts down on the high pressure switch.  The service person may not see the higher discharge pressure if the service port is in the liquid line which is normally downstream from the liquid line filter drier in split systems.  A pressure port installed in the hot gas discharge line, just as it exits the compressor, is required to see true discharge pressure.




IMPORTANT:  The compressor has an internal relief valve (IPRV) that is designed to open if the system is subjected to a high pressure situation.  Example causes are:  overcharged, air in system, restriction, factory installed metering device screens not removed and cleaned, old liquid line filter left in the system, poor airflow across the condenser, condenser fan failure, poor airflow across the evaporator in the heating mode (dirty return air filter(s)), poor system design (duct system undersized), etc.  The IPRV will open when the discharge pressure exceeds the suction pressure by more than 450 psi (smaller than 15-ton products) or 400 psi (larger than 15-ton products).  If the relief valve opens, a high velocity gas flow may be heard inside the compressor housing.  In some cases, the relief may open so quickly due to a restriction in the system, the high pressure will be difficult to observe on standard gauges.  In most instances, if the service person installs a discharge service gauge on the discharge line just as it exists the compressor, the development of high pressure can be observed before the relief valve opens.  Installing the discharge service gauge on the liquid line outside the system may not detect a restriction.  To reset the relief valve, shut the compressor off for a couple of minutes, allowing pressures to equalize.



REVIEW ALL SEVENTEEN STEPS TO MAKE SURE NOTHING WAS OVERLOOKED.

	Summary of Electronic Modules XE "Module Electrical Schematics and Other Information:Summary of Electronic Modules" 

	Bristol P/N
	Replace with Bristol P/N
	Vendor P/N
	Supply Voltage
	Output
	Sensors*
	Rtrip (()
	Reset
	Delay After Break
	LVCO
	Short Sensor
	248XXX Schematic Decals
	Screw
	Connector Wires

	241073
	None
	10AA307
	24
	Voltage
	Series
	25K-35K
	Auto
	No
	No
	Yes
	obsolete
	201125
	obsolete

	241283
	None
	10AA309
	24
	Voltage
	Series
	25K-35K
	Manual
	Yes    (lock out)
	No
	Yes
	obsolete
	201125
	obsolete

	241317
	None
	15AA1500A
	24
	Control
	Parallel
	10K-18K
	Manual
	Yes    (lock out)
	No
	Yes
	obsolete
	201126
	241353

	241359
	241731 or 241744
	15AA1000A
	24
	Control
	Parallel
	10K-18K
	Auto
	No
	No
	Yes
	obsolete
	201126
	241353

	241373
	241732 or 241742
	15AA1106A
	24
	Control
	Series
	26K-34K
	Auto
	Yes
	No
	Yes
	obsolete
	201126
	651043

	241374
	241733 or 241743
	15AA1607B
	120
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	651043

	241375
	241734 or 241743
	15AA1607C
	208/230
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	651043

	241376
	241732 or 241742
	MP50-9401
	24
	Control
	Series
	26K-34K
	Auto
	Yes
	No
	Yes
	obsolete
	201126
	651043

	241377
	241733 or 241743
	MP50-8601
	120
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	651043

	241378
	241734 or 241743
	MP50-8801
	208/230
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	651043

	241379
	241731 or 241744
	15AA1105A
	24
	Control
	Parallel
	10K-16K
	Auto
	Yes
	No
	Yes
	obsolete
	201126
	241353

	241380
	241745
	15AA1606B
	120
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	241353

	241381
	241745
	15AA1606C
	208/230
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	241353

	241382
	241731 or 241744
	MP50-9201
	24
	Control
	Parallel
	10K-16K
	Auto
	Yes
	No
	Yes
	obsolete
	201126
	241353

	241383
	241745
	MP50-8001
	120
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	241353

	241384
	241745
	MP50-8201
	208/230
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	241353

	241559
	241743
	15AA1706C
	208/230
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	241353

	241560
	241734 or 241743
	15AA1707C
	208/230
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	651043

	241679
	241731
	31AA1105A
	24
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	No
	053,508,509,510
	201126
	241353

	241680
	241745
	31AA1606E
	120&208/230
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	No
	051,052
	201126
	241353

	241696
	241732
	30AA200A
	24
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	053,508,509,510
	201126
	651043

	241697
	241733 or 241743
	30AA300B
	120
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	051,052
	201126
	651043

	241698
	241734 or 241743
	30AA300C
	208/230
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	051,052
	201126
	651043

	241730
	241745
	AE7114
	120&208/230
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	obsolete
	201126
	241353

	241731
	241770
	AE7113
	24
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	Yes
	053,508,509,510
	201126
	241353

	241732
	241772
	AE7110
	24
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	051,052
	201126
	651043

	241733
	241774
	AE7111
	120
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	051,052
	201126
	651043

	241734
	241774
	AE7112
	208/230
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	051,052
	201126
	651043

	241744
	241770
	41AA1105A
	24
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	No
	obsolete
	201126
	241353

	241745
	241771
	41AA1606E
	120&208/240
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	No
	511,512,513,514
	201126
	241353

	241770
	
	INT 369 R
	24
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	No
	511,512,513
	201126
	241353

	241771
	
	INT 369 R
	120 & 240
	Control
	Parallel
	10K-16K
	Auto
	Yes
	Yes
	No
	511,512,513
	201126
	241353

	241772
	
	INT 169 R
	24
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	052
	201126
	651043

	241774
	
	INT 169 R
	120 & 240
	Control
	Series
	26K-34K
	Auto
	Yes
	Yes
	No
	052
	201126
	651043


*Series – 7 1/2, 8 1/2, 10 ton

  Parallel – 12, 15, 17, 20, 24 ton



“G” COMPRESSOR WIRING DIAGRAM (DUAL POWER TERMINAL MODELS)

(WITH AE, 31AA or 41AA MODULE) - PARALLEL MODULE (4 SENSOR PINS) XE "15AA, MP50, AE, 31AA or 41AA Protection Modules (Parallel Sensors) - Dual Power Terminal, Full and Part Winding Start Models" 



[image: image3.wmf]S1

 

S2

 

S3

 

T1

 

T3

 

T2

 

 POWER

 

TERMINAL

 

 POWER

 

TERMINAL

 

T7

 

T9

 

T8

 

PROTECTION

 

 TERMINAL

 

TO CONTROL CIRCUIT

 

(M1

-

M2 CONTROL TO

 

BE PLACED IN SERIES

 

WITH CONTACTOR COIL)

 

C

 

HI

 

ORANGE

 

BLACK

 

LO

 

M1

 

M2

 

L2

 

L1

 

MODULE SUPPLY VOLTAGE

 

TO T7, T9, T8

 

OF CONTACTOR

 

TO T1, T3, T2

 

OF CONTACTOR

 

2.5 AMPS MAX

 

(SEE MODULE SUMMARY ON 

PAGE 10 FOR APPLICABLE 

PART 

N

UMBERS)

     

 








“G” COMPRESSOR WIRING DIAGRAM (DUAL POWER TERMINAL MODELS)

(WITH AE, 31AA OR 41AA MODULE) - PARALLEL MODULE (4 SENSOR PINS) XE "15AA, MP50, AE, 31AA or 41AA (Parallel Sensors) - Dual Power Terminal (WYE-Delta) Models" 





[image: image4.wmf]S1

 

S2

 

S3

 

T1

 

T3

 

T2

 

 POWER

 

TERMINAL

 

 POWER

 

TERMINAL

 

T6

 

T5

 

T4

 

PROTECTION

 

 TERMINAL

 

TO CONTROL CIRCUIT

 

(M1

-

M2 CONTROL TO

 

BE PLACED IN SERIES

 

WITH CONTACTOR COIL)

 

C

 

HI

 

ORANGE

 

BLACK

 

LO

 

M1

 

M2

 

L2

 

L1

 

MODULE SUPPLY VOLTAGE

 

(

SEE MODULE SUMMARY ON 

PAGE 10 FOR APPLICABLE 

PART NUMBERS)

 

TO T6, T5, T4

 

OF CONTACTOR

 

TO T1, T3, T2

 

OF CONTACTOR

 

2.5 AMPS MAX

 







“G” COMPRESSOR WIRING DIAGRAM (SINGLE POWER TERMINAL MODELS)

(WITH AE, 31AA OR 41AA MODULE) - PARALLEL MODULE (4 SENSOR PINS) XE "15AA, MP50, AE, 31AA or 41AA Protection Modeules (Parallel Sensors) - Single Power Terminal Models" 













“G” COMPRESSOR WIRING DIAGRAM (SINGLE POWER TERMINAL MODELS)

(WITH AE, 30AA OR 40AA MODULE) - SERIES MODULE (2 SENSOR PINS) XE "15AA, MP50, AE, 31AA and 41AA Modules (Parallel Sensors) - Two-Speed Models" 














“G” COMPRESSOR WIRING DIAGRAM (TWO SPEED MODELS)

(WITH AE, 31AA OR 41AA MODULE) - PARALLEL MODULE (4 SENSOR PINS)












[image: image5.wmf] 

IMPORTANT

:

  Bristol recommends a 4

-

minute 

delay on break anti

-

short cycling time delay to 

prevent contactor chattering.

 

 

Control voltage (thru M1

-

M2 on module) can be 

different from module supply voltage (L1

-

L2).  

Voltage to L1

-

L2 must be as marked on mo

dule.

 

 

“HI” and “LO” connections apply only on 120V and 

208/240V modules.

 

 

Crankcase heater must be connected to 

c

ontinuous power source.

 




“G” COMPRESSOR WIRING DIAGRAM (TWO SPEED MODELS)

(WITH AE, 30AA OR 40AA MODULE) - SERIES MODULE (2 SENSOR PINS)













 “G” SERIES INTERNAL LINE BREAK

(COMPARED TO MODULE PROTECTED H2NG SERIES PRODUCTS)

[image: image6.wmf]Housing Height in Inches

Suction Tube Height in Inches

Housing Diameter in Inches

Models

H2NG

H2BG

H25G

H2NG

H2BG

H25G

H2NG

H2BG

H25G

094

17.1

17.6

18.4

9

9

16

12.4

12.4

12.4

104

17.9

18.4

19.6

9

9

17.2

12.4

12.4

12.4

124

17.9

18.4

20.4

9

9

18

12.4

12.4

12.4

144

---

---

20.6

---

---

18.2

---

---

12.4



[image: image7.wmf]H

 

H

 

H

 

"G" COMPRESSOR

 

HOUSING CONFIGURATION

 

H*NG

 

MODULE PROTECTION

 

H*BG

 

INTERNAL LINE BREAK

 

H*5G

 

INTERNAL LINE BREAK

 

SUCTION

 

HEIGHT

 

HEIGHT

 

SUCTION

 

HEIGHT

 

SUCTION

 

(FIGURE 1)

 

HSG DIA

 

HSG DIA

 

HSG DIA

 


NOTE:  2nd digit defines refrigerant, i.e., 2 = R22 and 7 = R407C.

The H*BG and H*5G single speed compressors have internal line break protection and do not require a module. They are available in the 094, 104 and 124 models (also 144 in H*5G).  The H*BG models are physically identical to the old H*NG solid-state protector models except for a new smaller terminal box and a slight increase in height as shown in Figure 1.  The only installation change needed when replacing an H*NG with an H*BG is a minor wiring modification.  The H*5G models are physically identical to the H*BG except for suction tube location and an increase in housing height.

NOTE:
The H*5G has higher efficiency than the H*NG or H*BG and offers the 12 ton (H*5G144) with “internal line break” protection.

Procedure for replacement of H*NG single speed with H*BG or H*5G single speed models (when module is used as motor protection only and is not controlled by thermostat), see page 18 if module is controlled by the thermostat.

1.
Remove the wires originally run from the line or transformer to terminals L1 and L2 on the solid state module.

2.
Connect the two wires together that were originally run to terminals M1 and M2 on the solid state module.

3.
The only wires connected to the H*BG compressor will be the three power terminal leads and the crankcase heater leads.
REPLACING “H*NG” WITH “H*BG” OR “H*5G” - WHERE THE SYSTEM

THERMOSTAT IS USED TO CONTROL THE MODULE

“G” COMPRESSOR - WIRING DIAGRAM
(Single Power Terminal Models)

4.
Check for correct contactor sizes:



Minimum Contactor Size
Minimum Contactor Size

Model
230 Volt
460 Volt 
Model
230 Volt
460 Volt

H*BG094
30 Amp
20 Amp
H*5G094
35 Amp
20 Amp


H*BG104
35 Amp
20 Amp
H*5G104
40 Amp
25 Amp


H*BG124
40 Amp
20 Amp
H*5G124
50 Amp
30 Amp





H*5G144
50 Amp
30 Amp 



[image: image8.wmf] 

T1

 

T2

 

T4

 

T5

 

T3

 

T6

 

T1

 

T2

 

T3

 

T4

 

T5

 

T6

 

L1

 

L2

 

L3

 

L1

 

L2

 

L3

 

CS

 

CF

 

LOW SPEED

 

HIGH SPEED

 

NO CONNECTION

 

ON 

LOW SPEED

 



PARTS AND ACCESSORIES

FOR “G” SERIES COMPRESSORS
	PART NUMBER
	DESCRIPTION
	   MODEL

	250507 (344029)*
	Discharge Service Valve 7/8”
	(094-144)

	250508 (344030)*
	Suction Service Valve 1 1/8”
	(094-124)

	250509 (344031)*
	Discharge Sweat Adapter 7/8”
	(094-144)

	250510 (344032)*
	Suction Sweat Adapter 1 1/8”
	(094-124)

	250511
	Discharge Seal
	(094-294)

	250512
	Suction Seal
	(094-294)

	250527 (344035)*
	Discharge Service Valve 1 1/8”
	(184-294)

	250525 (344033)*
	Suction Service Valve 1 3/8”
	(144)

	250526 (344034)*
	Suction Service Valve 1 5/8”
	(184-294)

	250530 (344037)*
	Discharge Sweat Adapter 3/4” - 90°
	(094-144)

	250533 (344038)*
	Suction Sweat Adapter 1 3/8” - 90°
	(144)

	250534 (344039)*
	Discharge Adapter 1 1/8”
	(184-294)

	250529 (344036)*
	Suction Adapter 1 3/8”
	(144)

	309008
	Mounting Parts (Set 236203 Grommet Sleeve 236400)
	(094-124)

	309009
	Mounting Parts (Set 236205 Grommet Sleeve 226260)
	(144-294)

	241711
	Crankcase Heater 115V
	(094-124)

	241712
	Crankcase Heater 230V
	(094-124)

	241713
	Crankcase Heater 460V
	(094-124)

	241714
	Crankcase Heater 575V
	(094-124)

	241703
	Crankcase Heater 115V
	(144)

	241705
	Crankcase Heater 460V
	(144)

	241708
	Crankcase Heater 115V
	(184-294)

	241707
	Crankcase Heater 230V
	(184-294)

	241706
	Crankcase Heater 460V
	(184-294)

	241710
	Crankcase Heater 575V
	(184-294)

	241730
	Module 115/230V (Replaces 241380, 241381 and 241680)
	(184-294)

	241731
	Module 24V (Replaces 241379 and 241679)
	(184-294)

	241732
	Module 24V (Replaces 241373 and 241696)
	(094-124)

	241733
	Module 115V (Replaces 241374 and 241697)
	(094-124)

	241734
	Module 230V (Replaces 241375 and 241698)
	(094-124)

	241744
	Module 24V (Replaces 241379, 241679 and 241731)
	(184-294)

	241745
	Module 115/230V (Replaces 241380, 241381, 241680 and 241730)
	(184-294)

	241770
	Module 24V (Replaces 241379, 241679, 241731 and 241744)
	(184-294)

	241771
	Module 120/240V (Replaces 241380, 241381, 241680, 241730 and 241745)
	(184-294)

	241772
	Module 24V (Replaces 241373, 241696 and 241732)
	(094-124)

	241774
	Module 120/240V (Replaces 241374, 241375, 241697, 241698, 241733 and 241734
	(094-124)

	*Note:  (344_ _ _) part number includes Teflon seal


“G” SERIES ROTALOCK ADAPTER INFORMATION

[image: image9.wmf] 

250529

 

     

 

250510

 

250533

 

  

 

SUCTION ADAPTERS

 

DISCHARGE ADAPTERS

 

250508

 

250525

 

250509

 

250534

 

250530

 

SUCTION

 

VALVE

 

DISCHARGE

 

VALVE

 

250507

 

250527

 

A

 

B

 

C

 

A

 

B

 

D

 

C

 

C

 

B

 

E

 

D

 

B

 

A

 

B

 

C

 

A

 

B

 

C

 

A

 

B

 

C

 

D

 

C

 

B

 

D

 

A

 

E

 

A

 

A

 

250526

 

A

 

DISCHARGE SEAL

 

250511

 

SUCTION SEAL

 

250512

 

A

 

C

 


	BRISTOL PART NO.
	DESCRIPTION
	A
	B
	C
	D
	E

	250508 (344030)*
	Suction Valve
	1 1/8
	3
	7 3/16
	2 1/2
	1 3/4-12 UNF

	250511
	Discharge Seal
	1
	
	For 1 1/4”-12” UNF
	
	

	250512
	Suction Seal
	1 1/2
	
	For 1 3/4”-12” UNF
	
	

	250525 (344033)*
	Suction Valve
	1 3/8
	3 5/16
	7 3/16
	2 1/2
	1 3/4-12 UNF

	250526 (344034)*
	Suction Valve
	1 5/8
	3 1/2
	7 3/16
	2 1/2
	1 3/4-12 UNF

	250529 (344036)*
	Suction Adapter Straight
	1 3/8
	2 1/2
	1 3/4-12 UNF
	
	

	250510 (344032)*
	Suction Adapter Straight
	1 1/8
	2 3/16
	1 3/4-12 UNF
	
	

	250533 (344038)*
	Suction Adapter 90°
	1 3/8
	2 3/16
	1 3/4-12 UNF
	2 3/8
	

	250507 (344029)*
	Discharge Valve
	7/8
	2 11/32
	5 11/32
	2 1/64
	1 1/4-12 UNF

	250527 (344035)*
	Discharge Valve
	1 1/8
	19/32
	5 11/32
	2 5/32
	1 1/4-12 UNF

	250509 (344031)*
	Discharge Adapter Straight
	7/8
	1 23/32
	1 1/4-12 UNF
	
	

	250534 (344039)*
	Discharge Adapter Straight
	1 1/8
	2
	1 1/4-12 UNF
	
	

	250530 (344037)*
	Discharge Adapter 90°
	3/4
	1 13/16
	1 1/4-12 UNF
	1 9/16
	

	NOTE:  (344_ _ _) part number includes Teflon seal


COMPRESSORS WITH SWEAT FITTINGS CANNOT BE ADAPTED TO ROTALOCKS.

MOUNTING HOLE DIMENSIONS

[image: image10.wmf]PLAIN

WASHER

HOLD DOWN BOLT

MOUNTING

BASE (REF)

HEX NUT

LOCK WASHER

SLEEVE

7 1/2 THRU 10 TON:

9

1

2

"

COMPRESSOR

MOUNTING FOOT

(REF)

9

1

2

"

10

1

2

"

12 THRU 24 TON:

10

1

2

"

RUBBER MOUNT


NOTE:
RUBBER MOUNT IS SHOWN IN NON-COMPRESSED FORM.  TIGHTEN HOLD DOWN BOLT UNTIL BOTTOMED-OUT AGAINST SLEEVE.


PED LABEL INFORMATION

Explanation of the European Pressure Equipment Directive (PED) label information (if the compressor is PED-approved):

· The first five digits of the 11-digit serial number give the manufacture and leak test date of the compressor.  The first three digits represent the day of the year (for example, 059 = February 28).  The next two digits represent the year (for example, 02 = 2002).


· PS is the maximum allowable pressure


· PT is the leak test pressure


· TS (max) is the maximum design temperature


· TS (min) is the minimum design temperature
PRESSURE-TEMPERATURE RELATION CHART
	
	TEMPERATURE  °F
	
	
	TEMPERATURE  °F

	
	
	
	
	
	R404A
	R-407C
	
	
	
	
	
	
	R404A
	R-407C

	
	
	
	
	
	Saturated    
	Saturated
	Saturated 
	
	
	
	
	
	
	Saturated 
	Saturated
	Saturated 

	PSIG
	R-22
	R-502
	R-12
	134a
	Vap/Liq.
	Vapor 
	Liquid 
	
	PSIG
	R-22
	R-502
	R-12
	134a
	Vap/Liq.
	Vapor 
	Liquid 

	5*
	-48
	-57
	-29
	-22
	-57
	-41.0
	-54.0
	
	56
	31
	23
	58
	59
	20
	34.9
	23.4

	4*
	-47
	-55
	-28
	-21
	-56
	-39.5
	-52.6
	
	58
	32
	24
	60
	60
	22
	36.4
	24.9

	3*
	-45
	-54
	-26
	-19
	-54
	-38.1
	-51.2
	
	60
	34
	26
	62
	62
	23
	37.8
	26.3

	2*
	-44
	-52
	-25
	-18
	-53
	-36.8
	-49.8
	
	62
	35
	27
	64
	64
	25
	39.2
	27.8

	1*
	-43
	-51
	-23
	-16
	-52
	-35.5
	-48.5
	
	64
	37
	29
	65
	65
	26
	40.6
	29.2

	0
	-41
	-50
	-22
	-15
	-50
	-34.2
	-47.2
	
	66
	38
	30
	67
	66
	27
	42.0
	30.6

	1
	-39
	-47
	-19
	-12
	-48
	-31.8
	-44.7
	
	68
	40
	32
	68
	68
	29
	43.3
	31.9

	2
	-44
	-52
	-25
	-10
	-46
	-29.5
	-42.3
	
	70
	41
	33
	70
	69
	30
	44.6
	33.3

	3
	-34
	-42
	-14
	-8
	-43
	-27.2
	-40.1
	
	72
	42
	34
	71
	71
	32
	45.9
	34.6

	4
	-32
	-40
	-11
	-5
	-41
	-25.1
	-37.9
	
	74
	44
	36
	73
	72
	33
	47.8
	36.5

	5
	-30
	-38
	-9
	-3
	-39
	-23.1
	-35.8
	
	76
	45
	37
	74
	73
	34
	48.4
	37.1

	6
	-28
	-36
	-7
	-1
	-37
	-21.1
	-33.8
	
	78
	46
	38
	76
	75
	35
	49.6
	38.4

	7
	-26
	-34
	-4
	1
	-35
	-19.3
	-31.9
	
	80
	48
	40
	77
	76
	37
	50.8
	39.6

	8
	-24
	-32
	-2
	3
	-33
	-17.5
	-30.1
	
	85
	51
	43
	81
	79
	40
	53.7
	42.6

	9
	-22
	-30
	0
	5
	-32
	-15.7
	-28.3
	
	90
	54
	46
	84
	82
	42
	56.5
	45.4

	10
	-20
	-29
	2
	7
	-30
	-14.0
	-26.6
	
	95
	56
	49
	87
	85
	45
	59.2
	48.2

	11
	-19
	-27
	4
	8
	-28
	-12.4
	-24.9
	
	100
	59
	51
	90
	88
	48
	61.8
	50.9

	12
	-17
	-25
	5
	10
	-27
	-10.8
	-23.3
	
	105
	62
	54
	93
	90
	50
	64.3
	53.5

	13
	-15
	-24
	7
	12
	-25
	-9.2
	-21.7
	
	110
	64
	57
	96
	93
	52
	66.7
	56.0

	14
	-14
	-22
	9
	13
	-23
	-7.7
	-20.1
	
	115
	67
	59
	99
	96
	55
	69.1
	58.4

	15
	-12
	-20
	11
	15
	-22
	-6.3
	-18.6
	
	120
	69
	62
	102
	98
	57
	71.4
	60.8

	16
	-11
	-19
	12
	16
	-20
	-4.8
	-17.2
	
	125
	72
	64
	104
	100
	59
	73.6
	63.0

	17
	-9
	-18
	14
	18
	-19
	-3.5
	-15.8
	
	130
	74
	67
	107
	103
	62
	75.8
	65.3

	18
	-8
	-16
	15
	19
	-18
	-2.1
	-14.4
	
	135
	76
	69
	109
	105
	64
	77.9
	67.5

	19
	-7
	-15
	17
	21
	-16
	-0.8
	-13.0
	
	140
	78
	71
	112
	107
	66
	80.0
	69.6

	20
	-5
	-13
	18
	22
	-15
	0.5
	-11.7
	
	145
	81
	73
	114
	109
	68
	82.0
	71.7

	21
	-4
	-12
	20
	24
	-14
	1.8
	-10.4
	
	150
	83
	75
	117
	112
	70
	83.9
	73.7

	22
	-3
	-11
	21
	25
	-12
	3.0
	-9.2
	
	155
	85
	77
	119
	114
	72
	85.8
	75.7

	23
	-1
	-9
	23
	26
	-11
	4.2
	-7.9
	
	160
	87
	80
	121
	116
	74
	87.7
	77.6

	24
	0
	-8
	24
	27
	-10
	5.4
	-6.7
	
	165
	89
	82
	123
	118
	76
	89.5
	79.5

	25
	1
	-7
	25
	29
	-9
	6.6
	-5.5
	
	170
	91
	83
	126
	120
	78
	91.3
	81.3

	26
	2
	-6
	27
	30
	-8
	7.7
	-4.3
	
	175
	92
	85
	128
	122
	80
	93.1
	83.2

	27
	4
	-5
	28
	31
	-6
	8.9
	-3.2
	
	180
	94
	87
	130
	123
	82
	94.8
	84.9

	28
	5
	-3
	29
	32
	-5
	10.0
	-2.1
	
	185
	96
	89
	132
	125
	83
	96.5
	86.7

	29
	6
	-2
	31
	33
	-4
	11.0
	-1.0
	
	190
	98
	91
	134
	127
	85
	98.1
	88.4

	30
	7
	-1
	32
	35
	-3
	12.1
	0.1
	
	195
	100
	93
	136
	129
	87
	99.8
	90.1

	31
	8
	0
	33
	36
	-2
	-13.2
	1.2
	
	200
	101
	95
	138
	131
	88
	101.4
	91.8

	32
	9
	1
	34
	37
	-1
	14.2
	2.2
	
	205
	103
	96
	140
	132
	90
	102.9
	93.4

	33
	10
	2
	35
	38
	0
	15.2
	3.3
	
	210
	105
	98
	142
	134
	92
	104.5
	95.0

	34
	11
	3
	37
	39
	1
	16.2
	4.3
	
	220
	108
	101
	145
	137
	95
	107.4
	98.1

	35
	12
	4
	38
	40
	2
	17.2
	5.3
	
	230
	111
	105
	149
	140
	98
	110.3
	101.1

	36
	13
	5
	39
	41
	3
	18.1
	6.3
	
	240
	114
	108
	152
	143
	101
	113.1
	104.1

	37
	14
	6
	40
	42
	4
	19.1
	7.2
	
	250
	117
	111
	156
	146
	104
	115.9
	106.9

	38
	15
	7
	41
	43
	5
	20.0
	8.2
	
	260
	120
	114
	159
	149
	107
	118.5
	109.7

	39
	16
	8
	42
	44
	6
	20.9
	9.1
	
	275
	124
	118
	163
	153
	111
	122.3
	113.7

	40
	17
	9
	43
	45
	7
	21.8
	10.1
	
	290
	128
	122
	168
	157
	115
	126.0
	117.6

	42
	19
	11
	45
	47
	8
	23.6
	11.9
	
	305
	132
	126
	172
	161
	118
	129.5
	121.3

	44
	21
	13
	47
	49
	10
	25.4
	13.6
	
	320
	136
	130
	177
	165
	122
	132.9
	124.9

	46
	23
	15
	49
	51
	12
	27.1
	15.4
	
	335
	139
	133
	181
	169
	126
	136.2
	128.4

	48
	24
	16
	51
	52
	14
	28.7
	17.0
	
	350
	143
	137
	185
	172
	129
	139.4
	131.8

	50
	26
	18
	53
	54
	16
	30.3
	18.7
	
	365
	146
	140
	188
	176
	132
	142.5
	135.0

	52
	28
	20
	55
	56
	17
	31.9
	20.3
	
	
	
	
	
	
	
	
	

	54
	29
	21
	57
	57
	19
	33.4
	21.9
	
	
	
	
	
	
	
	
	

	*Inches of Mercury
	
	NOTE:  FOR REFRIGERANT BLENDS (R404A, R-407C)
   To determine superheat, use saturated vapor values (small figures)

   To determine subcooling, use saturated liquid values (BOLD figures)


CAUTION:  Bristol compressors are completely interchangeable with other manufacturers.  However, electrical specifications, tubing configurations, and wiring connections may vary.  Before installing and starting this compressor, you must review the wiring diagrams and check for correct electrical components.








WARNING:  The air conditioning unit is a pressurized system and hazards exist which could result in personal injury.  It is therefore required that the following steps for troubleshooting removal and installation of the hermetic compressor be performed by qualified personnel only.





WARNING:  Never use oxygen to pressurize a refrigeration or air conditioning system.  Oxygen can explode on contact with oil and could cause personal injury.  When using high pressure gas such as nitrogen or CO2 for this purpose, be sure to use a regulator that can control the pressure down to 1 or 2 psig.





WARNING:  	To avoid electrical shock, power to the compressor should remain off during performance of Steps 2 thru 14. 








CAUTION:  A Teflon seal is factory installed on the face of the suction and discharge line rotalock fitting of the compressor.  Use care not to damage this seal while removing the shipping plug or attaching the suction line.  Also, be sure to check the shipping plug once it has been removed to ensure that part of the plug did not remain in the compressor.











CAUTION:  Do not use the Bristol replacement compressor as an evacuation assist and never apply voltage to a compressor while it is in a vacuum as  damage could result to the compressor.











WARNING:  Voltage should not be applied to the compressor with the terminal cover and retainer(s) removed as personal injury could result.





MODULE





 





#4





 





 





#5





 





#2





 





THERMOSTAT





 





HI-LO CONNECTIONS APPLY ONLY TO AE OR 31AA





MODULE SUPPLY VOLTAGE


  24V - No additional wiring


120V - Jumper terminal LO to L2 terminal


230V - Jumper terminal HI to L2 terminal





IMPORTANT:  Bristol recommends a 4-minute delay on break anti-short cycling time delay to prevent contactor chattering.





Control voltage (thru M1-M2 on module) can be different from module supply voltage (L1-L2).  Voltage to L1-L2 must be as marked on module.





“HI” and “LO” connections apply only on 120V and 208/240V modules.





Crankcase heater must be connected to continuous power source.





MODELS:


H2NG204FR


H2NG244FR


H2NG294FR


(Part Winding Start)





H25G204DP


(Full Winding Start)





Voltages:


230/208 3-Phase





MODELS:


H*5G204LP


H*5G244LP


H*5G294LP





Voltages:


230/208 3-PH


460 3-PH





MOTOR PROTECTION SYSTEM





Modules have a 4 minute delay upon interruption of L1-L2 supply or after any fault condition occurs.





To prevent short cycling of compressor, wire high/low pressure switch and other safety switches in series with L1 or L2 power terminal on module.





WARNING:  Turn power off before checking sensors.  Allow unit to cool for 1-hour minimum.  Disconnect module from terminals.  Check sensors resistance using ohmmeter with 6-volt maximum supply.  Cold resistance range:  From common pin (top left) to each of the other three pins.


Supplier #1:  30-100 ohms


Supplier #2:  500-2500 ohms


See caution below!








POWER CIRCUIT (WYE-DELTA MODELS)





CAUTION:  AE and 31AA module common (“C”) sensor terminal internally connected to line voltage, can be “hot” to ground.





WARNING:  Compressor terminals must be wired in phase for proper operation.





Phase 1 - T1 & T6


Phase 2 - T2 & T4


Phase 3 - T3 & T5





Wye-Delta Connection:


Run (Delta) - 1 & 6, 2 & 4, 3 & 5


Start (Wye) - 1, 2, 3 (4, 5, 6 together)





HI-LO CONNECTIONS APPLY ONLY TO AE OR 31AA





MODULE SUPPLY VOLTAGE


  24V - No additional wiring


120V - Jumper terminal LO to L2 terminal


230V - Jumper terminal HI to L2 terminal





IMPORTANT:  Bristol recommends a 4-minute delay on break anti-short cycling time delay to prevent contactor chattering.





Control voltage (thru M1-M2 on module) can be different from module supply voltage (L1-L2).  Voltage to L1-L2 must be as marked on module.





“HI” and “LO” connections apply only on 120V and 208/240V modules.





Crankcase heater must be connected to continuous power source.





MODELS:


H2NG204FR


H2NG244FR


H2NG294FR


(Part Winding Start)





H25G204DP


(Full Winding Start)





Voltages:


230/208 3-Phase





MODELS:


H*NG144DP


H*NG184DP


H*5G184DP





Voltages:


230/208 3-PH





H*NG144DP


H*NG184DP


H*NG204DR


H*NG244DR


H*NG294DP


H*5G184DP


H*5G204DP


H*5G244DP


H*5G294DP





Voltages:


460 3-PH


575 3-PH





H*NG204DR


H*NG244DR





Voltages:


380 3-PH





MODELS:


H2NG144GP


H2NG184GP


H2NG204GP


H2NG244GP





Voltages:


230/208 3-Phase


460 3-Phase


575 3-Phase





MOTOR PROTECTION SYSTEM





Modules have a 4-minute delay upon interruption of L1-L2 supply or after any fault condition occurs.





To prevent short cycling of compressor, wire high/low pressure switch and other safety switches in series with L1 or L2 power terminal on module.





WARNING:  Turn power off before checking sensors.  Allow unit to cool for 1-hour minimum.  Disconnect module from terminals.  Check sensors resistance using ohmmeter with 6-volt maximum supply.  Cold resistance range:  From common pin (top left) to each of the other three pins.


Supplier #1:  30-100 ohms


Supplier #2:  500-2500 ohms


See caution below!





MOTOR PROTECTION SYSTEM





Modules have a 4 minute delay upon interruption of L1-L2 supply or after any fault condition occurs.





To prevent short cycling of compressor, wire high/low pressure switch and other safety switches in series with L1 or L2 power terminal on module.





WARNING: Turn power off before checking sensors.  Allow unit to cool for 1-hour minimum.  Disconnect module from terminals.  Check sensors resistance using ohmmeter with 6-volt maximum supply. Cold resistance range:  From common pin (top left) to each of the other three pins.


Supplier #1:  30-100 ohms


Supplier #2:  500-2500 ohms


See caution below!





IMPORTANT:  Bristol recommends a 4-minute delay on break anti-short cycling time delay to prevent contactor chattering.





Control voltage (thru M1-M2 on module) can be different from module supply voltage (L1-L2).  Voltage to L1-L2 must be as marked on module.





Crankcase heater must be connected to continuous power source.





MODELS:


H*NG094DP


H*NG104DR


H*NG124DP





Voltages:


230/208 3-PH


460 3-PH


575 3-PH





MOTOR PROTECTION SYSTEM





Modules have a 4-minute delay upon interruption of L1-L2 supply or after any fault condition occurs.





To prevent short cycling of compressor, wire high/low pressure switch and other safety switches in series with L1 or L2 power terminal on module.





WARNING:  Turn power off before checking sensors.  Allow unit to cool for 1-hour minimum.  Disconnect module from terminals.  Check sensors resistance using ohmmeter with 6-volt maximum supply.  Cold resistance range:


Supplier #1:  90-300 ohms


Supplier #2:  1500-7500 ohms





POWER CIRCUIT

















CAUTION:  AE and 30AA module (“S1”) sensor terminals are internally connected to line voltage, can be “hot” to ground.





POWER CIRCUIT


(Full and Part-Winding Start Models)





CAUTION:  AE and 31AA module common (“C”) sensor terminal internally connected to line voltage, can be “hot” to ground.





WARNING:  Compressor terminals must be wired in phase for proper operation.





PHASE 1 - T1 & T7


PHASE 2 - T2 & T8


PHASE 3 - T3 & T9





MODELS:


H*NG094GP


H*NG104GP


H*NG124GP





Voltages:


230/208 3-PH


460 3-PH


575 3-PH





MOTOR PROTECTION SYSTEM





Modules have a 4 minute delay upon interruption of L1-L2 supply or after any fault condition occurs.





To prevent short cycling of compressor, wire high/low pressure switch and other safety switches in series with L1 or L2 power terminal on module.





WARNING:  Turn power off before checking sensors.  Allow unit to cool for one hour minimum.  Disconnect module from terminals.  Check sensors resistance using ohmmeter with 6 volt maximum supply.  Cold resistance range:  From common pin (top left) to each of the other three pins.


Supplier #1:  90-300 ohms


Supplier #2:  1500-7500 ohms





POWER CIRCUIT





CAUTION:  AE and 30AA module (“S1”) sensor terminals are internally connected to line voltage, can be “hot” to ground.





HIGH SPEED





 





L2





WIRING A TWO-SPEED “G” FOR SINGLE-SPEED OPERATION





WARNING:  Cannot use ICM parallel motor protection modules, part numbers 241730 or 241731, with Kriwan sensors (cold resistance of 30-100 ohms for parallel sensors) because the modules have “shorted sensor protection” that does not allow operation below 500 ohms.





!!  BEFORE A SUSPECT COMPRESSOR IS REMOVED, ALWAYS CHECK LOCKED ROTOR PULL-DOWN VOLTAGE  !!


SEE PAGE 4 FOR DETAILS





IMPORTANT:  Bristol recommends a 4 minute delay on break anti-short cycling time delay to prevent contactor chattering.





Control voltage (thru M1-M2 on module) can be different from module supply voltage (L1-L2).  Voltage to L1-L2 must be as marked on module.





Crankcase heater must be connected to continuous power source.





 





MODULE SUPPLY VOLTAGE





 





PART NUMBERS





PAGE 10 FOR APPLICABLE 





 SUMMARY ON 





MODULE





SEE 





 





POWER





 





LOW SPEED





 





2.5 AMPS MAX





 





POWER





CAUTION:


ICM modules (part numbers 241730 and 241731) cannot be used with Kriwan sensors (30-100 ohms, cold).





 





POWER CIRCUIT





CAUTION:  AE or 31AA module common (“C”) sensor terminal internally connected to line voltage, can be “hot” to ground.





MOTOR PROTECTION SYSTEM





Modules have a 4-minute delay upon interruption of L1-L2 supply or after any fault condition occurs.





To prevent short cycling of compressor, wire high/low pressure switch and other safety switches in series with L1 or L2 power terminal on module.





WARNING:  Turn power off before checking sensors.  Allow unit to cool for 1-hour minimum.  Disconnect module from terminals.  Check sensors resistance using ohmmeter with 6-volt maximum supply.  Cold resistance range:  From common pin (top left) to each of the other three pins.


Supplier #1:  30-100 ohms


Supplier #2:  500-2500 ohms


See caution below!





POWER CIRCUIT

















CAUTION:  AE and 31AA module common (“C”) sensor terminal internally connected to line voltage, can be “hot” to ground.





Page 11





200023


EN Release 097X01


EN Revision P31703


3/07





Page 3





Page 4





S1





Page 10





MODELS:


H*NG204FR


H*NG244FR


H*NG294FR


(Part Winding Start)





H*5G204DP


(Full Winding Start)





Voltages:


230/208 3-PH





HI-LO CONNECTIONS APPLY ONLY TO AE OR 31AA





MODULE SUPPLY VOLTAGE


  24V - No additional wiring


120V - Jumper terminal LO to L2 terminal


230V - Jumper terminal HI to L2 terminal





IMPORTANT:   Bristol recommends a 4-minute delay on break anti-short cycling time delay to prevent contactor chattering.





Control voltage (thru M1-M2 on module) can be different from module supply voltage (L1-L2).  Voltage to L1-L2 must be as marked on module.





“HI” and “LO” connections apply only on 120V and 208/240V modules.





Crankcase heater must be connected to continuous power source.





CAUTION:


ICM modules (part numbers 241730 and 241731) cannot be used with Kriwan sensors (30-100 ohms, cold).








CAUTION:


ICM modules (part numbers 241730 and 241731) cannot be used with Kriwan sensors (30-100 ohms, cold).








CAUTION:


ICM modules (part numbers 241730 and 241731) cannot be used with Kriwan sensors (30-100 ohms, cold).





S2





 





WARNING:  Do not remove the rotalock caps without first relieving the dry air charge in the compressor by carefully loosening the 1/4” flare suction access port cap to allow slow release of all pressure.





 





S1





 





T1





 





T3





 





T2





 





 POWER





 





TERMINAL





 





 POWER





 





TERMINAL





 





T4





 





T6





 





T5





 





PROTECTION





 





 TERMINAL





 





TO CONTROL  CIRCUIT





 





(M1





-





M2 CONTROL TO





 





BE PLACED IN SERIES





 





WITH CONTACTOR COIL)





 





C





 





HI





 





ORANGE





 





BLACK





 





LO





 





M1





 





M2





 





L1





 





 





S2





 





S3





 





 POWER





 





TERMINAL





 





T1





 





T3





 





T2





 





PROTECTION





 





 TERMINAL





 





TO CONTROL CIRCUIT





 





(M1





-





M2 CONTROL TO





 





BE PLACED IN SERIES





 





WITH CONTACTOR COIL)





 





C





 





ORANGE





 





BLACK





 





L2





 





 





 





L1





 





L2 L1 M2 M1





 





MODULE SUPPLY VOLTAGE


(SEE MODULE SUMMARY ON PAGE 10 FOR APPLICABLE PART NUMBERS)








 





 





S1





 





 





 





 POWER





TERMINAL





 





 





 





TO T1, T3, T2





 





OF CONTACTOR





 





2.5 AMPS MAX





 





 





T1





 





T3





 





T2





 





PROTECTION





 





 TERMINAL





 





TO CONTROL CIRCUIT





 





(M1





-





M2 CONTROL TO





 





BE PLACED IN SERIES





 





WITH CONTACTOR COIL)





 





S2





 





M2





 





M1





 





MODULE SUPPLY VOLTAGE


(SEE MODULE SUMMARY ON PAGE 10 FOR APPLICABLE PART NUMBERS)





 





S3





HI-LO CONNECTIONS APPLY ONLY TO AE OR 31AA





MODULE SUPPLY VOLTAGE


  24V - No additional wiring


120V - Jumper terminal LO to L2 terminal


230V - Jumper terminal HI to L2 terminal





 





 





 





 





 





 





 TERMINAL





PROTECTION





TO CONTROL CIRCUIT





 





TO T1, T2, T3





 





OF CONTACTOR





 





2.5 AMPS MAX





 





 





(M1





-





M2 CONTROL TO





 





BE PLACED IN SERIES





 





WITH CONTACTOR COIL)





 





S1





 





S2





 





L2





 





L1





 





2.5 AMPS MAX





 





M1





 





M2





 





 POWER





 





TERMINAL





 





T4





 





T5





 





T6





 





 POWER





 





TERMINAL





 





T1





 





T2





 





T3





 





HIGH





 





 





 





SPEED





 





POWER





 





LOW





 





 





 





SPEED





 





POWER





 





MODULE SUPPLY VOLTAGE SEE MODULE SUMMARY ON PAGE 10 FOR APPLICABLE PART NUMBERS





 





THERMOSTAT





 





#1





 





5G





 





*





 





BG and H





*





H





 





24 VOLT POWER





 





 





PROTECTION





 





  SAFETY





 





PRESSURE





 





 





HIGH/LOW





 





 





 





 





CONTACTOR COIL





 





  COMPRESSOR





 





M





 





#2





 





#5





 





#4





 





#3





 





#1





 





NG





*





H





 





24 VOLT POWER





 





PROTECTION





 





  SAFETY





 





PRESSURE





 





HIGH/LOW





 





M2





 





L2





 





M1





 





L1





 





CONTACTOR COIL





 





  COMPRESSOR





 





M





H*BG





H*NG





OF CONTACTOR





TO T1, T3, T2





WIRING





COMPRESSOR INTERNAL





LINE BREAK





INTERNAL





T1





T3





T2





MOTOR





MODULE SUPPLY VOLTAGE





TO CONTROL CIRCUIT





OF CONTACTOR





TO T1, T3, T2





MODULE





C (OR S)





S1





L2





L1





M1





M2





T1





T3





T2





PROTECTION


FUSITE


TERMINAL





MOTOR





T2





MOTOR





MODULE SUPPLY VOLTAGE





TO CONTROL CIRCUIT





OF CONTACTOR





TO T1, T3, T2





MODULE





C (OR S)





S1





M1





M2





T1





T3





T2





MOTOR





H*BG





H*NG





OF CONTACTOR





TO T1, T3, T2





WIRING





COMPRESSOR INTERNAL





LINE BREAK





INTERNAL





T1





T3








Page 15

_893152826

_1150696835.doc


TAKE SUCTION 







TEMPERATURE







6" TO 12"







FROM COMPRESSOR







NOTE:







 58°F







-38°F







 20°F







FOR THE HARD TO GET







TO COMPRESSOR TAKE







TEMPERATURES AND







PRESSURES HERE,







AIR CONDITIONING







UNIT ONLY







CONVERT SUCTION







    PRESSURE TO







    TEMPERATURE







65 PSIG = 38°F (3°C)







 







     SUPERHEAT







HOW TO CHECK SUPERHEAT







58°F







  DIGITAL







THERMOMETER







(14° C)







 (11°K)







(- 3°C)







 (14°C)












_1150702807.unknown

_1172412066

_1235914434.doc


IMPORTANT:  Bristol recommends a 4-minute delay on break anti-short cycling time delay to prevent contactor chattering.







Control voltage (thru M1-M2 on module) can be different from module supply voltage (L1-L2).  Voltage to L1-L2 must be as marked on module.







“HI” and “LO” connections apply only on 120V and 208/240V modules.







Crankcase heater must be connected to continuous power source.












_1151738299.xls
Sheet1

				Housing Height in Inches						Suction Tube Height in Inches						Housing Diameter in Inches

		Models		H2NG		H2BG		H25G		H2NG		H2BG		H25G		H2NG		H2BG		H25G

		94		17.1		17.6		18.4		9		9		16		12.4		12.4		12.4

		104		17.9		18.4		19.6		9		9		17.2		12.4		12.4		12.4

		124		17.9		18.4		20.4		9		9		18		12.4		12.4		12.4

		144		---		---		20.6		---		---		18.2		---		---		12.4



&A

Page &P




_1153566197.doc


250529







     







250510







250533







  







SUCTION ADAPTERS







DISCHARGE ADAPTERS







250508







250525







250509







250534







250530







SUCTION







VALVE







DISCHARGE







VALVE







250507







250527







A







B







C







A







B







D







C







C







B







E







D







B







A







B







C







A







B







C







A







B







C







D







C







B







D







A







E







A







A







250526















SUCTION SEAL







250512







250511







DISCHARGE SEAL







A







C











A












_1150702699.unknown

_893153022

_893757832

_1065012866.doc


NO CONNECTION



ON LOW SPEED







HIGH SPEED







LOW SPEED







CF







CS







L3







L2







L1







L3







L2







L1







T6







T5







T4







T3







T2







T1







T6







T3







T5







T4







T2







T1












_893156193

_893152836

_893152804

_893152815

_851157060

_893146333

